Date: Feb 19, 2026

Title: RFP #20261362620 Cooling Tower Upgrades (JPOC 1400)

Subject: Addendum to RFP

#### The following is hereby added to the initial RFP for further consideration.

All corrections, changes, additions, revisions, and/or clarifications in this Addendum #1 to the

RFP are hereby made a part of RFP #20261362620 Cooling Tower Upgrades (JPOC 1400).

All Respondents to the RFP shall acknowledge receipt and acceptance of this Addendum #1 by

signing in the space provided and submitting the signed Addendum #1 with the RFP.

Proposals submitted without an executed copy of this Addendum #1 attached may be considered

informal and may be rejected.

Received, acknowledged, and conditions agreed to on this _________ day of _________, 2026, by:

Respondent:  __________________________________________________________

Company Name: _______________________________________________________

If there are questions pertaining to this addendum please contact: Bid_submissions@jpshealth.org

- MINIMUM REQUIREMENTS

The contractor shall provide all labor, materials, equipment, and supervision necessary to complete the following scope of work for the cooling tower refurbishment:

1.	Lockout/Tagout and Shutdown Coordination

•	Perform lockout/tagout of all fan motors and electrical equipment.

•	Coordinate with others for the shutdown of condenser water pumps, fans, and/or chillers, as required.

•	Contractor is responsible for performing a pre-tab test prior to start of project and performing a post tab after the project is completed ensuring that systems are designed to specifications.

•	Contractor is responsible to provide a project manager to be site for the length of the project to ensure detail and optimum performance for the scope of work being performed.

- Contractor shall provide a third-party commission team to verify the programming, controls, building automation and performance per the specifications of the design.

2.	Fan Section Removal

•	Set up the crane and remove the fan section for temporary on-site storage.

•	All crane operations shall be conducted after hours.

3.	Demolition and Disposal

•	Remove and properly dispose of the existing filling material, drift eliminators from both cells, and any other parts being replaced.

4.	Structural Components

•	Furnish and install new galvanized steel end and side panels for the fill sections in both cells.

•	Furnish and install new fill supports and top internal supports for distribution piping.

•	Furnish and install new ladders and platforms on cooling tower for motor access.

•	Contractor shall clean, grit blasting, welding and apply special coating to steel and metal surfaces.

5.	Spray System

•	Furnish and install new spray manifold boxes on both cells.

•	Install new spray piping.

•	Install new piping for the CW for the cooling tower that supplies the building.

•	Furnish and install installation on all new piping for cooling tower.

•	Install heat trace on the CW piping that supplies the building.

6.	Fill and Drift Eliminators

•	Furnish and install new PVC fill material and top PVC drift eliminators, water distribution systems (nozzles) and drive components.

7.	Mechanical Components

•	Furnish and install two (2) new shaft kits, including shafts, bearings, pulleys, VFDs and motors.

•	Reinstall the existing fan blades and furnish new fan belts.

•	Provide alternate for removal of belt drive and installation of direct or gear drive.

8.	Basin and Controls

•	Furnish and install two (2) existing VFDs with new ones.

•	Furnish and install two (2) new basin heaters with control sensors.

•	Furnish and install two (2) new float valve assemblies.

•	Furnish and install new gaskets, leak sealing and apply coating to basin to ensure all leaks are sealed.

9.         Controls and BAS Integration

•	Coordinate with CLIMATEC to integrate the new cooling tower into the existing Building Automation System (BAS).

•	Verify all control points, alarms, and sequences of operation during startup and commissioning.

10.	Startup, Testing, and Commissioning

•	Coordinate with the manufacturer’s authorized representative for factory startup and testing.

•	Perform operational verification, system balancing, and commissioning to confirm performance per design specifications.

•	Provide on-site training for JPS operations and maintenance staff upon project completion.

•	Deliver all as-built drawings, O&M manuals, warranties, and startup reports to JPS Facilities at turnover.

11.   Contractor Deliverables

•	Lift plan and rigging plan for equipment removal and installation.

•	Safety plan and ICRA documentation.

•	Commissioning plan and startup checklist.

•	As-built drawings (mechanical, electrical, and controls).

•	O&M manuals and manufacturer warranty documentation.

•	Pre and Post TAB reports provided to JPS Leadership.

•	Training session for JPS maintenance staff on all new installed equipment and CLIMATEC controls that serve the equipment.

12. Warranty

•	Provide two (2) year parts and labor warranty covering all materials and workmanship.