Date: May 6, 2026

Title: RFP #20261378859 Cooling Tower & Chiller Replacement (JPOC 1400)

Subject: Revision to RFP

#### The following is hereby added to the initial RFP for further consideration.

All corrections, changes, additions, revisions, and/or clarifications in this Addendum #2 to the

RFP are hereby made a part of RFP #20261378859 Cooling Tower & Chiller Replacement (JPOC 1400).

All Respondents to the RFP shall acknowledge receipt and acceptance of this Addendum #2 by

signing in the space provided and submitting the signed Addendum #2 with the RFP.

Proposals submitted without an executed copy of this Addendum #2 attached may be considered

informal and may be rejected.

Received, acknowledged, and conditions agreed to on this _________ day of _________, 2026, by:

Respondent:  __________________________________________________________

Company Name: _______________________________________________________

If there are questions pertaining to this addendum please contact: Bid_submissions@jpshealth.org

- PROJECT SCOPE #1 Cooling Tower Replacement

JPS is requesting the replacement of the two EVAPCO cooling towers located at the JPOC 1400 Building (located at 1400 South Main Street, Fort Worth, TX 76104). This proposal includes complete tower replacement with new fill and fill supports, galvanized panels, spray piping supports, shaft kits, basin heaters, control sensors, fill valves, BAS, drift eliminators, motors, bearings, pulleys, belts, platforms and ladders, VFDs, and insulation for all associated piping back to the building. Cooling Tower Fan Direct Drive add alternate is required.

- MINIMUM REQUIREMENTS

The contractor shall provide all labor, materials, equipment, and supervision necessary to complete the following scope of work for the cooling tower refurbishment:

1.	Lockout/Tagout and Shutdown Coordination

•	Perform lockout/tagout of all fan motors and electrical equipment.

•	Coordinate with others for the shutdown of condenser water pumps, fans, and/or chillers, as required.

2.	Fan Section Removal

•	Set up the crane and remove the fan section for temporary on-site storage.

•	All crane operations shall be conducted after hours.

3.	Demolition and Disposal

•	Remove and properly dispose of the existing filling material, drift eliminators from both cells, and any other parts being replaced.

4.	Structural Components

•	Furnish and install new galvanized steel end and side panels for the fill sections in both cells.

•	Furnish and install new fill supports and top internal supports for distribution piping.

5.	Spray System

•	Furnish and install new spray manifold boxes on both cells.

•	Install new spray piping.

6.	Fill and Drift Eliminators

•	Furnish and install new PVC fill material and top PVC drift eliminators in both cells.

7.	Mechanical Components

•	Furnish and install two (2) new shaft kits, including shafts, bearings, pulleys, VFDs and motors.

•	Install new fan blades and furnish new fan belts.

•	Provide and install direct drive or gear drive.

8.	Basin and Controls

•	Furnish and install two (2) new VFDs and integrated into Climatic controls BAS.

•	Furnish and install two (2) new basin heaters with control sensors.

•	Furnish and install two (2) new CDW pumps.

•	Furnish and install two (2) new VFD’s for cooling tower.

•	Furnish and install two (2) new float valve assemblies.

•	Furnish and install (2) ladders with platforms on all sides of cooling towers.

•	Provide temporary chiller for duration of project.

•	Remove and replace pump concrete pads.

9.Startup, Testing, and Commissioning

•	Coordinate with the manufacturer’s authorized representative for factory startup and testing.

•	Perform operational verification, system balancing, and commissioning to confirm performance per design specifications.

•	Provide on-site training for JPS operations and maintenance staff upon project completion.

•	Deliver all as-built drawings, O&M manuals, warranties, and startup reports to JPS Facilities at turnover.

10.Contractor Deliverables

•	Lift plan and rigging plan for equipment removal and installation.

•	Safety plan and ICRA documentation.

•	Commissioning plan and startup checklist.

•	As-built drawings (mechanical, electrical, and controls).

•	O&M manuals and manufacturer warranty documentation.

•	Training session for JPS maintenance staff.

11.	Warranty

•	Provide two (2) year parts and labor warranty covering all materials and workmanship.

- PROJECT SCOPE #2 Chiller Replacement

The purpose of this project is to remove and replace the existing 185-ton centrifugal chillers (Chiller #1 and 2) located at JPOC 1400 (1400 South Main Street, Fort Worth, TX 76104). The new chillers will serve critical healthcare areas and are intended to improve system reliability, energy efficiency, and serviceability.

All work must be performed in accordance with healthcare facility construction standards, ASHRAE guidelines, local mechanical and electrical codes, and manufacturer installation requirements.

Work shall be executed with minimal disruption to ongoing healthcare operations and coordinated closely with JPS Facilities staff.

- MINIMUM REQUIREMENTS

General Requirements

•	Contractor shall visit the site prior to bid submission to verify existing conditions.

•	All work shall comply with OSHA safety standards, infection control risk assessment (ICRA) requirements, and the facility’s hot work, lockout/tagout, and shutdown procedures.

•	Contractor is responsible for obtaining all necessary permits, inspections, and approvals.

•	Any power, water, or HVAC shutdowns must be coordinated and approved in advance by JPS Facilities.

•	Contractor shall provide detailed lift plans, rigging diagrams, and safety plans for all crane activities.

•	All materials and workmanship shall be in accordance with the latest industry standards and manufacturer recommendations.

•	Contractor shall maintain a clean, organized, and safe job site throughout the duration of the project.

Scope of Work

A. Demolition and Removal

•	Isolate and lock out all utilities serving the existing chillers.

•	Remove all electrical, chilled water (CHW), and condenser water (CW) piping back to the first set of isolation valves.

•	Safely prepare, disconnect, and remove the existing (2) 185-ton centrifugal chiller using approved lifting and rigging methods, coordinated with JPS Facilities.

•	Remove and dispose of all demolished materials in accordance with local environmental regulations.

B. Installation of New (2) Chillers

•	Furnish and install (2) new high-efficiency centrifugal chiller (Trane or York, Carrier, Daikin or Equivalent) of equal or greater capacity.

•	Rig and set the new chillers in the designated penthouse mechanical area per manufacturer guidelines.

•	Fabricate and install new CHW and CW piping from the new chiller to the existing isolation valves, including all required fittings, supports, and anchors and pump replacement for chillers.

•	Replace existing isolation control valves.

•	Replace existing CHW pumps.

•	Replace or remove existing pads for pumps.

•	Replace and reconnect and reconfigure existing electrical power, including conduit, wiring, and disconnects, as required for the new equipment.

•	Replace and connect and reconfigure refrigerant relief piping to the new chillers per code.

•	Provide new pipe and insulation on all new piping and replace existing insulation.

•	Provide new louver on penthouse wall.

•	Provide new air intake hood on exterior of the penthouse.

•	Restore any disturbed walls, floors, or penetrations to pre installation conditions, including firestopping with STI products and finishes.

•	Temporary chiller in place for duration of project.

C. Controls and BAS Integration

•	Coordinate with CLIMATEC to integrate the new chillers into the existing Building Automation System (BAS).

•	Verify all control points, alarms, and sequences of operation during startup and commissioning.

D. Startup, Testing, and Commissioning

•	Coordinate with the manufacturer’s authorized representative for factory startup and testing.

•	Perform operational verification, system balancing, and commissioning to confirm performance per design specifications.

•	Provide on-site training for JPS operations and maintenance staff upon project completion.

•	Deliver all as-built drawings, O&M manuals, warranties, and startup reports to JPS Facilities at turnover.

________________________________________

E. Work Schedule and Logistics

•	All crane, rigging, and lifting operations shall occur on weekend days or as scheduled with JPS Facilities to minimize impact to operations.

•	Contractor shall coordinate delivery routes, staging areas, and temporary closures with JPS and Security.

•	Work hours and access restrictions shall comply with facility requirements.

•	Temporary barriers, signage, and protection shall be provided to ensure safe pedestrian and staff access around the work area.

________________________________________

F. Contractor Deliverables

•	Lift plan and rigging plan for equipment removal and installation.

•	Safety plan and ICRA documentation.

•	Commissioning plan and startup checklist.

•	As-built drawings (mechanical, electrical, and controls).

•	O&M manuals and manufacturer warranty documentation.

•	Training session for JPS maintenance staff.

________________________________________

G. Preferred Equipment

•	Manufacturer: Trane or York or Equivalent.

•	Type: High-efficiency centrifugal chiller.

•	Capacity: 185 tons (nominal).