- Within our current Water Safety scope, the Nalco team completes monthly temperature, chlorine, pH monitoring on domestic cold and hot water systems at the Main hospital and quarterly sampling for offsites. Shall this be included in RFP? If so, what line is it best to allocate these fees to?  Yes, it should be included under Water Quality Monitoring Program

- Located in Lot 1, Section D, should there be a separate line item for HPC routine testing for SPD? HPC is a bacteria test is a part of AAMI ST108 for critical and utility water and is currently a part of the current Water Safety scope. Yes, it can be a separate line item.

- Located in Lot 2, section B: Closed loops and glycol. Once these systems are treated and if they continue to operate with no leaks, continual chemical additions are not needed. How would it be best to notate that chemical shall be ordered on an as needed basis and place a cost per 5gal pal of chemistry?  Evaluated semiannually.